## Calculator
Boulard 自然通風計算器（天窗＋左右側窗）
藍字為可修改輸入；開口比可輸入 0，代表該開口不存在。xlsm 為巨集啟用格式，但本計算器本身以公式計算。
輸入參數 |  |  |  | 計算結果
Floor area Af | 1000 | m² | 僅用於換算總風量 Q_total | Total side ratio As/Af | 0.4
Greenhouse height H | 4.5 | m | 平均高度；ACH = q / H | Ventilation mode | Roof + side
Side-to-roof height diff Hc | 3 | m | 側窗與天窗幾何中心垂直距離 | Epsilon ε | 0.42164
ΔT (indoor - outdoor) | 5 | °C | 室內外溫差 | Absolute rate q | 690.9766 | m³/m²·h
Outdoor temperature To | 303 | K | 絕對溫度，例如 30°C ≈ 303 K | ACH | 153.5503 | h⁻¹
Outdoor wind speed uw | 3 | m/s | 室外風速 | Total flow Q_total | 690976.5551 | m³/h
Roof vent ratio Ar/Af | 20% | ratio | 天窗開口比，可輸入 0 | Check 1
Left side vent ratio AL/Af | 20% | ratio | 左側側窗開口比，可輸入 0 | Check 2
Right side vent ratio AR/Af | 20% | ratio | 右側側窗開口比，可輸入 0
Cd (single-opening) | 0.64 | - | Case 1 單一開口係數 | Current formulas used
Cw (single-opening) | 0.1 | - | Case 1 風效應係數 | Case 1 (single opening): q = 1800*r*Cd*SQRT(2*g*(ΔT/To)*(H/4)+Cw*u²)
Cd*SQRT(Cw) (roof+side) | 0.2 | - | Case 2 全域係數 | Case 2 (roof + side): q = 1800*(Ar/Af+As/Af)*(Cd*SQRT(Cw))*SQRT(u² + (2*g*ε²/Cw)*(ΔT/To)*(Hc/2))
Cw (roof+side) | 0.07 | - | Case 2 風效應係數 | ε = SQRT(2)*rr*rs / ((rr+rs)*SQRT(rr²+rs²)); rs = 左右側窗開口比總和
Gravity g | 9.81 | m/s² | 常數；可保留 9.81 | When either roof or side total = 0, the sheet automatically switches to single-opening mode.

## Net_Impact
Boulard 自然通風 + 防蟲網影響估算器
藍字為可修改輸入。此頁會比較無防蟲網與有防蟲網時的絕對通風風量率、ACH，並用孔隙率估算防蟲網壓損。
Screen loss model is an engineering estimate: K_screen ≈ (1-φ²)/φ² ; larger screen area lowers face velocity and pressure drop.
General inputs |  |  |  | Results |  |  | Screen geometry and pressure-drop inputs
Floor area Af | 1000 | m² | Used to convert q to total Q | Total side ratio As/Af | 0.4 | ratio
Greenhouse height H | 4.5 | m | Average interior height | Ventilation mode | Roof + side
Side-to-roof height diff Hc | 3 | m | Vertical distance between side and roof vent centres | ε geometry factor | 0.42164
ΔT (indoor - outdoor) | 5 | °C | Indoor minus outdoor air temperature | q without screens | 690.9766 | m³/m²·h
Outdoor temperature To | 303 | K | Absolute outdoor temperature, e.g. 30°C ≈ 303 K | ACH without screens | 153.5503 | h⁻¹ |  | Screen area / opening area |  |  |  | no screen
Outdoor wind speed uw | 3 | m/s | Outside wind speed | Equivalent side-screen loss K_side | 1.5177 | - | roof | 1 | 2 | 4 | 5
Roof vent ratio Ar/Af | 0.2 | ratio | Can be 0 | Total screen loss K_total | 3.0354 | - | left side | 1 | 2 | 4 | 5
Left side vent ratio AL/Af | 0.2 | ratio | Can be 0 | Screen reduction factor | 0.4978 | - | right side | 1 | 2 | 4 | 5
Right side vent ratio AR/Af | 0.2 | ratio | Can be 0 | q with screens | 343.9715 | m³/m²·h | q with/wo screens | 343.9715 | 521.0151 | 633.4944 | 652.4997 | 690.9766
Cd (single opening) | 0.64 | - | Base coefficient without screen | ACH with screens | 76.4381 | h⁻¹ | ACH with/wo screens | 76.4381 | 115.7811 | 140.7765 | 144.9999 | 153.5503
Cw (single opening) | 0.1 | - | Base wind coefficient without screen | Ventilation reduction | 50.22% | %
Cd*SQRT(Cw) (roof+side) | 0.2 | - | Base global coefficient without screen | Total screen ΔP path | 0.00025979 | kPa
Cw (roof+side) | 0.07 | - | Base wind coefficient without screen | Total flow Q with screens | 343971.4734 | m³/h
Air density ρ | 1.2 | kg/m³ | Used for screen ΔP estimate
Gravity g | 9.81 | m/s² | Constant
[7 empty] | Vent | Open ratio | Preset ref | Mesh X (/in) | Mesh Y (/in) | dX (mm) | dY (mm) | Screen area / opening area | Pitch X (mm) | Pitch Y (mm) | Opening X (mm) | Opening Y (mm) | Porosity φ | K_screen raw | K_screen effective | Face velocity u_s (m/s) | ΔP (kPa)
[7 empty] | Roof | 0.2 | 40x25_0.16 | 40 | 25 | 0.16 | 0.16 | 1 | 0.635 | 1.016 | 0.475 | 0.856 | 0.63023 | 1.5177 | 1.5177 | 0.47774 | 0.00020783
[7 empty] | Left side | 0.2 | 40x25_0.16 | 40 | 25 | 0.16 | 0.16 | 1 | 0.635 | 1.016 | 0.475 | 0.856 | 0.63023 | 1.5177 | 1.5177 | 0.23887 | 5.1958e-05
[7 empty] | Right side | 0.2 | 40x25_0.16 | 40 | 25 | 0.16 | 0.16 | 1 | 0.635 | 1.016 | 0.475 | 0.856 | 0.63023 | 1.5177 | 1.5177 | 0.23887 | 5.1958e-05
How screen loss is applied
1) Base q uses the same Boulard formulas as the original workbook (no screen).
2) Porosity φ is calculated from mesh counts and wire diameters.
3) Raw loss coefficient uses K ≈ (1-φ²)/φ².
4) Effective loss is reduced by larger screen area: K_eff = K / (AreaFactor²).
5) For roof+side, total screen loss is approximated as roof loss + equivalent side loss.
6) ΔP is estimated from ΔP = 0.5·ρ·K·u_s² and shown in kPa.
Note on L22: Reference preset name only. Mesh counts and wire diameters remain manually editable; copy values from Insect_Net_Library if needed.
Note on V22: Porosity uses projected 2D opening area from mesh pitch and wire diameters. Formula form consistent with woven-screen geometry literature. Source URL in Notes.
Note on W22: Approximate porosity-only screen loss coefficient K ≈ (1-φ²)/φ²; analytical review notes this Brundrett-type porosity function is one commonly used option for screen pressure-drop modelling.
Note on X22: Effective K reduces with larger screen area because face velocity through the mesh falls roughly with area ratio.
Note on Z22: ΔP estimate uses 0.5*rho*K*u^2 and is shown in kPa. Greenhouse literature often reports screen pressure-drop coefficients and Cd reductions from wind-tunnel tests; use those if available.
Note on L23: Reference preset name only. Mesh counts and wire diameters remain manually editable; copy values from Insect_Net_Library if needed.
Note on L24: Reference preset name only. Mesh counts and wire diameters remain manually editable; copy values from Insect_Net_Library if needed.

## Batch_Cases
Batch scenario table (copy row 5 downward to compare multiple cases)
Editable inputs are blue. You can set any of Roof / Left / Right vent ratios to 0.
Case | Af | H | Hc | ΔT | To(K) | u_w | Roof | Left | Right | Cd1 | Cw1 | Cd√Cw_2 | Cw2 | As_total | Mode | ε | q (m³/m²·h) | ACH | Q_total (m³/h)
Default | 1000 | 4.5 | 3 | 5 | 303 | 3 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 690.9766 | 153.5503 | 690976.5551
Case 2 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 3 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 4 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 5 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 6 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 7 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 8 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 9 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Case 10 | [13 empty] | 0 | No opening |  | 0 | 0 | 0
Tip
For roof+side cases, set Hc explicitly. For roof-only or side-only cases, Hc is ignored.

## Notes
Notes / References
Usage | Enter vent ratios as fractions of floor area. Example: 20% = 0.20.
Vent handling | Roof, left side, and right side ratios all allow 0. The workbook automatically chooses no-opening, single-opening, or roof+side mode.
ACH | ACH = q / H, where q is in m³/m²·h and H is greenhouse average height in m.
Case 1 | Single-opening formula based on Boulard/Baille style expression with Cd and Cw.
Case 2 | Roof+side formula based on Boulard/Kittas style expression with ε geometry factor and Cd*SQRT(Cw).
Practical note | Case 2 still needs Cw separately because the buoyancy term contains 1/Cw inside the square root.
Source URL 1 | https://efwe.ukzn.ac.za/wp-content/uploads/2021/11/Thipe_EL.pdf
Source URL 2 | https://www.mdpi.com/2073-4395/12/9/1995
Source URL 3 | https://elibrary.asabe.org/abstract.asp?aid=21268
Default coefficients | Defaults are editable engineering starting values, not site-specific measurements.
Macro format | This workbook is saved as .xlsm. The calculator itself uses worksheet formulas, so calculations still work even if macros are not enabled in Excel.
Screen model | Added sheet Net_Impact estimates screen porosity from mesh count and wire diameter, computes an approximate screen-loss coefficient K ≈ (1-φ²)/φ², then reduces q and ACH with a simple series-loss approximation. Larger screen area lowers face velocity and reduces ΔP.
Source URL 4 | https://gala.gre.ac.uk/id/eprint/38584/7/38584_LAI_Semi_analytical_calculation_of_pore_related_parameters.pdf
Source URL 5 | https://www.insongreen.com/greenhouse-screens/
Source URL 6 | https://pmc.ncbi.nlm.nih.gov/articles/PMC4883381/
Caution | If manufacturer wind-tunnel data for Cd,φ or pressure-drop curves are available, those measured values are preferable to the porosity-only estimate used here.

## Insect_Net_Library
Commercial greenhouse insect-net examples
Reference examples from commercial catalog; users may copy/modify values into Net_Impact.
Preset | Mesh X (/inch) | Mesh Y (/inch) | Wire dia X (mm) | Wire dia Y (mm) | Opening X (mm) | Opening Y (mm) | Typical use | Source URL
32x25_0.15 | 32 | 25 | 0.15 | 0.15 | 0.6 | 0.83 | Standard / larger insects | https://www.insongreen.com/greenhouse-screens/
40x25_0.16 | 40 | 25 | 0.16 | 0.16 | 0.44 | 0.8 | Whitefly / aphid class | https://www.insongreen.com/greenhouse-screens/
50x25_0.19 | 50 | 25 | 0.19 | 0.19 | 0.29 | 0.78 | Finer exclusion | https://www.insongreen.com/greenhouse-screens/
60x30_0.16 | 60 | 30 | 0.16 | 0.16 | 0.25 | 0.67 | Anti-thrip / fine mesh | https://www.insongreen.com/greenhouse-screens/
60x40_0.16 | 60 | 40 | 0.16 | 0.16 | 0.25 | 0.46 | Very fine / high resistance | https://www.insongreen.com/greenhouse-screens/