## Calculator
Boulard 自然通風計算器（天窗＋左右側窗）
藍字為可修改輸入；開口比可輸入 0，代表該開口不存在。xlsm 為巨集啟用格式，但本計算器本身以公式計算。
輸入參數 |  |  |  | 計算結果
Floor area Af | 1000 | m² | 僅用於換算總風量 Q_total | Total side ratio As/Af | 0
Greenhouse height H | 4.5 | m | 平均高度；ACH = q / H | Ventilation mode | Single opening
Side-to-roof height diff Hc | 3 | m | 側窗與天窗幾何中心垂直距離 | Epsilon ε
ΔT (indoor - outdoor) | 5 | °C | 室內外溫差 | Absolute rate q | 259.0574 | m³/m²·h
Outdoor temperature To | 303 | K | 絕對溫度，例如 30°C ≈ 303 K | ACH | 57.5683 | h⁻¹
Outdoor wind speed uw | 3 | m/s | 室外風速 | Total flow Q_total | 259057.3865 | m³/h
Roof vent ratio Ar/Af | 20% | ratio | 天窗開口比，可輸入 0 | Check 1
Left side vent ratio AL/Af | 0% | ratio | 左側側窗開口比，可輸入 0 | Check 2
Right side vent ratio AR/Af | 0% | ratio | 右側側窗開口比，可輸入 0
Cd (single-opening) | 0.64 | - | Case 1 單一開口係數 | Current formulas used
Cw (single-opening) | 0.1 | - | Case 1 風效應係數 | Case 1 (single opening): q = 1800*r*Cd*SQRT(2*g*(ΔT/To)*(H/4)+Cw*u²)
Cd*SQRT(Cw) (roof+side) | 0.19579 | - | Case 2 全域係數 | Case 2 (roof + side): q = 1800*(Ar/Af+As/Af)*(Cd*SQRT(Cw))*SQRT(u² + (2*g*ε²/Cw)*(ΔT/To)*(Hc/2))
Cw (roof+side) | 0.07 | - | Case 2 風效應係數 | ε = SQRT(2)*rr*rs / ((rr+rs)*SQRT(rr²+rs²)); rs = 左右側窗開口比總和 | Case 2 的 Cd = 0.74
Gravity g | 9.81 | m/s² | 常數；可保留 9.81 | When either roof or side total = 0, the sheet automatically switches to single-opening mode.

## Batch_Cases
Batch scenario table (copy row 5 downward to compare multiple cases)
Editable inputs are blue. You can set any of Roof / Left / Right vent ratios to 0.
Case | Af | H | Hc | ΔT | To(K) | u_w | Roof | Left | Right | Cd1 | Cw1 | Cd√Cw_2 | Cw2 | As_total | Mode | ε | q (m³/m²·h) | ACH | Q_total (m³/h)
Default | 1000 | 4.5 | 3 | 5 | 303 | 2 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 494.1342 | 109.8076 | 494134.192
Case 2 | 1000 | 4.5 | 3 | 5 | 303 | 2 | 0% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Single opening |  | 402.8332 | 89.5185 | 402833.2137
Case 3 | 1000 | 4.5 | 3 | 5 | 303 | 2 | 20% | 0% | 0% | 0.64 | 0.1 | 0.2 | 0.07 | 0 | Single opening |  | 201.4166 | 44.7592 | 201416.6068
Case 4 | 1000 | 4.5 | 3 | 5 | 303 | 2 | 20% | 10% | 10% | 0.64 | 0.1 | 0.2 | 0.07 | 0.2 | Roof + side | 0.5 | 344.8324 | 76.6294 | 344832.3866
Case 5 | 1000 | 4.5 | 3 | 2 | 303 | 3 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 665.5237 | 147.8942 | 665523.7335
Case 6 | 1000 | 4.5 | 3 | 3 | 303 | 2 | 0% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Single opening |  | 362.4067 | 80.5348 | 362406.7069
Case 7 | 1000 | 4.5 | 3 | 3 | 303 | 2 | 20% | 0% | 0% | 0.64 | 0.1 | 0.2 | 0.07 | 0 | Single opening |  | 181.2034 | 40.2674 | 181203.3535
Case 8 | 1000 | 4.5 | 3 | 3 | 303 | 2 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 470.2667 | 104.5037 | 470266.6901
Case 9 | 1000 | 4.5 | 3 | 3 | 303 | 1 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 284.9259 | 63.3169 | 284925.8848
Case 10 | 1000 | 4.5 | 3 | 5 | 303 | 1 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 322.8012 | 71.7336 | 322801.1768
Case 11 | 1000 | 4.5 | 3 | 5 | 303 | 1 | 0% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Single opening |  | 313.9643 | 69.7699 | 313964.3388
Case 12 | 1000 | 4.5 | 3 | 5 | 303 | 1 | 20% | 0% | 0% | 0.64 | 0.1 | 0.2 | 0.07 | 0 | Single opening |  | 156.9822 | 34.8849 | 156982.1694
Case 13 | 1000 | 4.5 | 3 | 5 | 303 | 1 | 30% | 0% | 0% | 0.64 | 0.1 | 0.2 | 0.07 | 0 | Single opening |  | 235.4733 | 52.3274 | 235473.2541
Case 14 | 1000 | 4.5 | 3 | 5 | 303 | 0 | 20% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Roof + side | 0.42164 | 239.8846 | 53.3077 | 239884.555
Case 15 | 1000 | 4.5 | 3 | 5 | 303 | 0 | 0% | 20% | 20% | 0.64 | 0.1 | 0.2 | 0.07 | 0.4 | Single opening |  | 278.1006 | 61.8001 | 278100.5969
Case 16 | 1000 | 4.5 | 3 | 5 | 303 | 0 | 20% | 0% | 0% | 0.64 | 0.1 | 0.2 | 0.07 | 0 | Single opening |  | 139.0503 | 30.9001 | 139050.2985
Tip
For roof+side cases, set Hc explicitly. For roof-only or side-only cases, Hc is ignored.

## Notes
Notes / References
Usage | Enter vent ratios as fractions of floor area. Example: 20% = 0.20.
Vent handling | Roof, left side, and right side ratios all allow 0. The workbook automatically chooses no-opening, single-opening, or roof+side mode.
ACH | ACH = q / H, where q is in m³/m²·h and H is greenhouse average height in m.
Case 1 | Single-opening formula based on Boulard/Baille style expression with Cd and Cw.
Case 2 | Roof+side formula based on Boulard/Kittas style expression with ε geometry factor and Cd*SQRT(Cw).
Practical note | Case 2 still needs Cw separately because the buoyancy term contains 1/Cw inside the square root.
Source URL 1 | https://efwe.ukzn.ac.za/wp-content/uploads/2021/11/Thipe_EL.pdf
Source URL 2 | https://www.mdpi.com/2073-4395/12/9/1995
Source URL 3 | https://elibrary.asabe.org/abstract.asp?aid=21268
Default coefficients | Defaults are editable engineering starting values, not site-specific measurements.
Macro format | This workbook is saved as .xlsm. The calculator itself uses worksheet formulas, so calculations still work even if macros are not enabled in Excel.