## PF simulation
Plant | [10 empty] | CO2 balance | [6 empty] | CO2 Price |  |  |  | kg CO2 | cost,NT$ | Ratio
crop type (light) | std |  | Pm= | 0.24051 |  | Pmax= | 0.88 | mg/(m2.s) |  |  |  | CO2 supply to room (CS) |  |  | 67.9329 | mg/(s.room) |  | 20 |  | CO2 used | per day | 3.9129 | 78.2588 | 3.161% | -B=Ca+Kc+Rc*Pm | 2936.0599
crop type (CO2) | std |  | Rc= | 1407.6081 |  | Photosynthetic Capacity | [5 empty] | Net photos. rate in room (CN) |  |  | 52.74 | mg/(s.room) |  | NT$/kg |  |  | /day/plant | 0.00065216 | 0.013043 |  | 4*A*C = 4*Rc*Ca*Pm | 2921633.2916
KI | 100 | W/m2 | GI | 0.35211 | [7 empty] | CO2 loss by ventilation (CV) |  |  | 15.1929 | mg/(s.room) |  |  |  |  | /day/m2 room | 0.039129 |  |  | B^2 - 4*A*C = | 5698814.5343
Kc | 440 | mg/m3 | Gc | 0.77618 |  |  | Ps: | Photosynthesis | 0.19496 | mg/(m2.s) |  | CS = CN + CV | [8 empty] | per month | 117.3881 | 2347.7625
CO2 in chloroplast | 848.7 | ppm | 1525.9054 | mg/m3 |  |  | Rp: | Photorespiration | 0.0080602 | mg/(m2.s) | Water balance | [9 empty] | per year | 1428.2222 | 28564.4441
Tm | 25 |  | GTI | 1 |  |  | Rd: | Darkrespiration | 0.098995 | mg/(m2s) |  | Transpiration rate of room (TR) |  |  | 2795.8789 | mg/(s.room) |  | Elec.fee: Light |  |  |  |  | cost,NT$
a | 15 |  | Kpr | 0.041344 |  |  | Pn: | Net Photos. | 0.0879 | mg/(m2.s) |  | (De)Humidification (H) |  |  | -2621.5372 | mg/(s.room) |  | 3.5 |  | Light elec | 36.44 | kW/room
Rd(20C) | 0.07 |  | Q10 | 2 | [7 empty] | Water loss by ventilation (VW) |  |  | 174.3417 | mg/(s.room) |  | NT$/kWh |  |  | 583.04 | kWh per day | 2040.64 | 82.44%
Environment | T, deg.C |  | RH, % | density = 1/SV | VP, kPa | ah | Enthalpy,kJ/kg | VD, g/m3 | VDDleaf-air | VDDin-out |  | TR+H = VW | [6 empty] | Light Period |  | 0.097173 | kWh /day/plant
Leaf T | 25 | RH_leaf | 100 | 1.1439 | 3.1674 |  |  | 23.0096 | [10 empty] | 16 |  | 5.8304 | kWh/day/m2 room
indoor T | 25 | RH_in | 80 | 1.1439 | 2.5339 | 0.015953 | 65.7688 | 18.4076 | 4.6019 |  | Energy balance | [9 empty] | 17491.2 | kWh per month | 61219.2
outdoor T | 5 | RH_out | 40 | 1.2261 | 0.34891 | 0.0021491 | 10.4244 | 2.7169 |  | 15.6908 |  |  |  | k (conductivity of walls) = |  | 0.1 |  |  |  |  | 212809.6 | kWh per year | 744833.6
CO2 indoor (ppm) | 1200 | -> mg/m3 | 2157.5191 | 1.7979 |  | Pn/Tr = | 0.018863 | = Transpiration Efficiency (TE) |  |  |  | Total W of lamps (WL) |  |  | 36360 | W/room |  | Elec.fee: AC |  |  |  |  | cost,NT$
CO2 outdoor (ppm) | 410 | -> mg/m3 | 790.1563 | 1.9272 |  | Tr/Pn = | 53.0125 | Rav | 100 | s/m |  | Total W of other equipment (We) |  |  | 80 | W/room |  | 5.5 |  | AC_elec | 6.3667 | kW/room
Wind (m/s) | 1 | m/s | CropType | high | std | low |  | Rlv | 520.6522 | s/m |  | Heat loss by ventilation (Qv) |  |  | 703.4146 | W/room |  | COP |  |  | 101.8664 | kWh per day | 356.5325 | 14.4%
|  |  | Rlv = | 652.7174 | 520.6522 | 388.587 |  | Rlv.inc | 366.925 | s/m |  | Heat loss by conduction (Qc) |  |  | 720 | W/room |  |  |  |  | 0.016978 | kWh/day/plant
ACH | 0.1 | 1/h | CropType | std | low |  |  | Rv.total | 987.5772 | s/m |  | Heat carry away by AC (Qa) |  |  | 35016.5854 | W/room |  |  |  |  | 1.0187 | kWh/day/m2 room
|  |  | Rlv.inc = | 366.925 | 183.4625 |  |  | Tr | 4.6598 | mg/(m2.s) | [10 empty] | 3055.9929 | kWh per month | 10695.9752
Culture room | [11 empty] | WL + We = Qv + Qc + Qa | [8 empty] | 37181.2471 | kWh per year | 130134.3647
Room length | 10 | m | space utilization |  | 0.5 |  |  | Leaf area/plant | 0.1 | m2/plt | [7 empty] | Capacity of AC required |  |  | 9.9479 | RT, Note: 3.52 kW per Refri. Ton
Room width | 10 | m | No. of layers |  | 4 |  |  | Number of plants | 6000 | plt/room
Room height | 4 | m | Culture area |  | 200 | m2 |  | Total leaf area | 600 | m2 |  |  | Operating cost (CO2 + AC & Light Elec) | [7 empty] | EY | 100 | g/kWh
Room volume | 400 | m3 | Cropping density |  | 30 | plts/m2 |  | LAI | 3 |  |  |  |  | Ratio of OP cost |  |  | per day | 2475.4313 | NT$ |  | Yield | 58.304 | kg/day
Lighting | [12 empty] | ACH | CO2 | Light elec | AC elec | per month | 74262.9377 | NT$ |  |  | 1749.12 | kg/month
W per LEDtube | 20 | W/lamp | Number of LEDtubes |  | 1818 |  |  | PAR | 54.3478 | W/m2 |  |  | 0.1 | 3.161% | 82.44% | 14.4% | per year | 903532.4088 | NT$ |  |  | 20989.44 | kg/year
No.LEDtube/layer | 6 |  | PPFD |  | 250 | μmol/m2/s |  | DLI | 14.4 | mol/m2/day
Bench area per layer | 0.66 | m2 | Light Period |  | 16 | h/day | Power consump. / cural area |  | 181.8182 | W/m2
Total W of other equip (We) |  |  | 80 | W/room |  |  |  | Total W of lamps | 36360 | W/room

## CO2 balance
CO2 balance
LA per plant |  | 0.1 | m2/plant | CN per room | 52.74 | mg/s/room
Number of plants |  | 6000 | plants/room | CO2 absorbed by plants
Pn |  | 0.0879 | mg/m2/s
ACH |  | 0.1 | 1/h | CV per room | 15.1929 | mg/s/room
Room volumn |  | 400 | m3 | CO2 loss by ventilation
|  | ppm | mg/m3 | CS per room | 67.9329 | mg/s/room
CO2 in | @Tin | 1200 | 2157.5191 | CO2 supply to room
CO2 out | @Tout | 410 | 790.1563

## Water balance
| deg.C |  | % | density | VP, kPa | ah, kg/kg | Enthalpy,kJ/kg | VD, g/m3 | VDDleaf-air | VDDin-out
T_leaf | 25 | RH_leaf | 100 | 1.1439 | 3.1674 |  |  | 23.0096
T_in | 25 | RH_in | 80 | 1.1439 | 2.5339 | 0.015953 | 65.7688 | 18.4076 | 4.6019
T_out | 5 | RH_out | 40 | 1.2261 | 0.34891 | 0.0021491 | 10.4244 | 2.7169 |  | 15.6908
Water balance | [5 empty] | TR per room | 2795.8789 | mg/s/room
LAperPlt |  | 0.1 | m2/plant |  |  | Vapor transpired by plants
NoofPlts |  | 6000 | plants/room
Tr |  | 4.6598 | mg/m2/s |  |  | VW per room | 174.3417 | mg/s/room
ACH |  | 0.1 | 1/h |  |  | Vapor loss by ventilation
Room volumn |  | 400 | m3
TR + H = VW, or |  | H = Vw - TR |  |  |  | (De)H needed | -2621.5372 | mg/s/room
TR = Tr*LAperPlt*NoofPlts | [5 empty] | Value > 0 means Humidification
Vw=VolofRoom*ACH*(Vdin-Vdout)*1000/3600 | [5 empty] | Value < 0 means Dehumidification

## Energy balance
| deg.C |  | % | density | VP, kPa | ah, kg/kg | Enthalpy,kJ/kg | VD, g/m3 | VDDleaf-air | VDDin-out
T_leaf | 25 | RH_leaf | 100 | 1.1439 | 3.1674 |  |  | 23.0096
T_in | 25 | RH_in | 80 | 1.1439 | 2.5339 | 0.015953 | 65.7688 | 18.4076 | 4.6019
T_out | 5 | RH_out | 40 | 1.2261 | 0.34891 | 0.0021491 | 10.4244 | 2.7169 |  | 15.6908
Room dimension |  | Length | 10 | Width | 10 | Height | 4 | m
Room volume | 400 | m3 | ACH | 0.1 |  | kw (conductivity of walls) = |  |  | 0.1
Energy balance
WL + We = Qv + Qc + Qa
| Total W of lamps (WL) |  |  | 36360 | W/room, Total W of other equip. (We) |  |  |  | 80 | W/room
| Heat loss by ventilation (Qv) |  |  | 703.4146 | W/room
Qv = (Enth_in - Enth_out) * Density_in * VolofRoom * ACH / 3.6
| Heat loss by conduction (Qc) |  |  | 720 | W/room
Qc = 2*(Lg*Wid+Wid*Hgh+Lg*Hgh) * Kw * (Tin - Tout)
| Heat carry away by AC (Qa) |  |  | 35016.5854 | W/room
Qa = WL + We - Qv - Qc