## 說明
Notes |  | This is a planning tool to estimate relative changes in transpiration and dehumidification energy.
Calibrate 'Baseline_Water_L_per_m2_day' using your measured irrigation minus drainage (or condensate).
Within modest changes, transpiration roughly scales with VPD and stomatal/boundary-layer drivers.
|  |  | Blue fraction: +10% blue → ~+20% stomatal conductance (heuristic). |  | use 15% as the reference
CO2 enrichment 400→1000 ppm → ~30% reduction in stomatal conductance (heuristic).
Wind effect modeled as sqrt(u/0.2 m/s); keep airflow uniform to avoid tipburn.
Latent kWh = water_kg × 2450 kJ/kg ÷ 3600 ÷ COP_latent.
Replace defaults with your crop-specific data for accuracy.
| # Blue effect |  |  | def transpiration_index(VPD_kPa, blue_frac, co2_ppm, wind_mps):
| ref_blue = 0.15 |  |  | # Index ∝ VPD × multipliers above (no PPFD term; assume PPFD constant across scenarios)
| k_blue_per10 = 0.20 |  |  | return VPD_kPa * stomatal_multiplier(blue_frac, co2_ppm, wind_mps)
blue_effect = 1.0 + k_blue_per10 * ((blue_frac - ref_blue) / 0.10)
# CO2 effect
# Cap between 0.6 and 1.05 to avoid silly values
co2_effect = 1.0 - 0.30 * max(0.0, min(1.0, (co2_ppm - 400.0) / 600.0))
co2_effect = max(0.6, min(1.05, co2_effect))
# Wind effect ~ sqrt(u / 0.2)
wind_effect = math.sqrt(max(1e-6, wind_mps) / 0.2)
return blue_effect * co2_effect * wind_effect

## 輸入與計算
Transpiration Optimizer
「PFAL 降蒸散、維持生長」試算模板，含基準 vs. 優化兩組環控參數（CO₂、VPD、葉面風速、藍光比例）→ 估算蒸散量、除濕潛熱負荷與電費節省。
可以直接改表內的輸入值（尤其把「Baseline_Water_L_per_m2_day」改成你量到的日用水/冷凝水量），結果會即時更新。
輸入區 |  | 計算結果
Parameter | Value |  | Scenario | Transpiration_Index | Water_L_per_day | Latent_kWh_per_day | Elec_price USD per day
Area_m2 | 100 |  | Baseline | 1.319 | 225 | 85.0694 | 10.2083
Canopy_fraction | 0.9 |  | Optimized | 0.46921 | 80.04 | 30.262 | 3.6314
Elec_price_USD_per_kWh | 0.12 |  | Savings (Opt - Base) | -0.84979 | -144.96 | -54.8074 | -6.5769
COP_latent | 1.8 | 重現計算過程
Base_PPFD_umol | 240 |  | Blue fraction: +10% blue → ~+20% stomatal conductance (heuristic). |  |  |  |  | ref.blue | 0.15
Base_Blue_frac | 0.2 |  |  | Blue.base | 1.1 |  |  | k_blue_per10 | 0.2
Base_CO2_ppm | 450 |  |  | Blue.opt | 0.86 |  | blue_effect = 1.0 + k_blue_per10 * ((blue_frac - ref_blue) / 0.10)
Base_VPD_kPa | 1.1 |  | CO2 enrichment 400→1000 ppm → ~30% reduction in stomatal conductance (heuristic).
Base_Windspeed_mps | 0.25 |  |  | CO2.base | 0.975
Opt_PPFD_umol | 240 |  |  | CO2.opt | 0.7
Opt_Blue_frac | 0.08 |  | Wind effect modeled as sqrt(u/0.2 m/s); keep airflow uniform to avoid tipburn.
Opt_CO2_ppm | 1000 |  |  | Wind.base | 1.118
Opt_VPD_kPa | 0.9 |  |  | Wind.opt | 0.86603
Opt_Windspeed_mps | 0.15 |  | Within modest changes, transpiration roughly scales with VPD and stomatal/boundary-layer drivers.
Baseline_Water_L_per_m2_day | 2.5 |  |  | Tr.base | 1.319
|  |  |  | Tr.opt | 0.46921
Latent kWh = water_kg × 2450 kJ/kg ÷ 3600 ÷ COP_latent.