## PF CO2 Balance
CO2 balance in PFAL
| Length | Width | Height | Vr (m3)
Room | 10 | 10 | 5 | 500
| Temp., oC | RH, % | CO2, ppm | CO2.mg/m3
Indoor | 25 | 80 | 1000 | 1799.9056
Outdoor | 5 | 40 | 380 | 733.1702
Leaf Area, LA (m2/plant) | No. of plants (plant/room) | Pn (mg/m2s) | ACH | Cn, mg/(s room) | Cv, mg/(s room) | Cs, mg/(s room)
0.02 | 100 | 1 | 0.02 | 2 | 2.9632 | 4.9632
Cv = ACH/3600 x (CO2mgin - CO2mgout) x Vroom
Cn = Pn x L
Cs = Cn + Cv
CO2mg = CO2ppm x 44.01/22.4 x 273/(273+T)
Cv: Rate of CO2 release by air change, mg/s/room
Cn: Net photosynthetic rate per room, mg/s/room
Cs: CO2 supplied, mg/s/room
ACH: Air change per hour, 1/h
Vr: Volume of the room, m3
H/W/L: Height/Width/Length of the room, m
CO2mgin: indoor CO2 concentration in mg/m3
CO2mgout: outdoor CO2 concentration in mg/m3
Pn: Net photosynthetic rate per leave area, mg/m2/s
L: Total leaf area, m2/room

## PF water Balance
Water balance in PFAL
Leaf Area, LA (m2/plant) | Num. of plants (plant/room) | Tr (mg/m2s) | Dehumidification rate, mg/s/room | TR, mg/(s room) | Humidification rate, mg/s/room
0.02 | 100 | 1 | 0 | 2 | 41.5854
Room length (m) | Room width (m) | Room height (m) | Vr (m3)
10 | 10 | 5 | 500
| T | RH | Vd, g/m3 | Vw, mg/(s room)
indoor | 25 | 80% | 18.4076 | 43.5854
outdoor | 5 | 40% | 2.7169
ACH (1/h)
0.02
TR + H = D + Vw |  | H = D + Vw - TR
Vw = ACH/3600 x (Vd.in - Vd.out) x 1000 x Vr
TR = Tr x TLA
TR: Transpirate rate, mg/s/room
H: Rate of humidification, mg/s/room
D: Rate of dehumidification, mg/s/room
Vw: Rate of water vapor release by ventilation, mg/s/room
Tr: Transpiration rate per m2 of leaf, mg/m2/s
TLA = Total leaf area, m2
ACH: Air change per hour, 1/h
Vd: Vapor density, g/m3
Vr: interal volume, m3

## PF Energy Balance
Energy balance in PFAL
Patm (kpa) | 101.325
W per lamp | No. of lamps | Other equip., W | ACH, 1/h | Total W of lamps, W
20 | 400 | 0 | 0.02 | 8000
Room length, m | width, m | height, m |  | Vr, m3
10 | 10 | 5 |  | 500
| Temp., oC | RH, % | Vds, g/m3 | Vd, g/m3 | ρDA, kg/m3 | ρw, kg/m3 | Hs, kJ/kg | Hfg (kJ/kg) | HL, kJ/kg | VPs, kPa | VP, kPa | AH, kg/kg | h, kJ/kg
Indoor | 25 | 80% | 23.0096 | 18.4076 | 1.183 | 1.1829 | 25.75 | 2441.775 | 37.9975 | 3.1674 | 2.5339 | 0.015953 | 65.7688
Outdoor | 5 | 40% | 6.7922 | 2.7169 | 1.2681 | 1.183 | 5.15 | 2489.075 | 5.7166 | 0.87226 | 0.34891 | 0.0021491 | 10.4244
|  |  |  | QV, J/s room | QC, J/s room | QA, J/s room
Kw (J/s m2 C) | 0.1 |  |  | 181.8627 | 800 | 7018.1373
Cp, J/kg.K | 1030
HL = Hfg x Vd/1000 / ρair |  |  |  | WL + We = Qv + Qc + QA
Hs = T x Cp / 1000 |  |  |  | Qv = (hin - hout) x Rhoair x ACH x Vr x 1000/3600
Hfg=2500.9−2.365×T |  |  |  | Qc = Kw x Ar x (Tin - Tout)
QA = WL + We - Qv - Qc
HL: Latent heat, J/kg
Hfg: Vaporization heat of water, J/kg |  |  |  | WL: Electricity energy supplied to lamps, W
Vd: Water vapor density, g/m3 |  |  |  | We: Electricity energy supplied to other equipment in a room, W
ρair: Air density, kg/m3 |  |  |  | Qv: Heat by ventilation, W
Hs: Sensible heat gain, J/kg |  |  |  | Qc: Conduction heat, W
T: Temperature, oC |  |  |  | Qa: Heat removed by AC, W
Tin, Tout: Indoor, outdoor air Temp. |  |  |  | Kw: Overall conductivity of walls/roof/floor, W/m2.c
Cp: Specific heat, J/kg.K |  |  |  | Ar: Overall surface area of a room = 2 x (WxL+WxH+LxH), m2
hin, hout: Indoor, outdoor enthalpy, kJ/kg
ACH: Air change per hour, 1/h
Vr: Volume of a room = W x L x H, m3

## PF simulation
Simulation of a Plant Factory with Artificial Lighting (PFAL)
Plant | Pmax= | 2.66 |  | Pm= | 0.208 |  | -B=CO2mg+Kc+Rc*Pm |  | 2672.0389 |  | CO2 balance
| plant type (light) | std. |  | Rc= | 2077.549 |  | 4*Rc*CO2mg*Pm |  | 3111196.3543 |  |  | Net photos. rate in room (CN) |  | 0.08449 | mg/(s.room)
| plant type (CO2) | std. |  | GTL | 1 |  | A=Rc |  | 2077.549 |  |  | CO2 loss by ventilation (CV) |  | 2.9632 | mg/(s.room)
| KI | 100 |  | GL | 0.10072 |  | Ps =(-B-sqrt(B2-4AC))/(2A) |  |  |  |  | CO2 supply to room (CS) |  | 3.0476 | mg/(s.room)
| Kc | 440 |  | Gc | 0.77638 | [6 empty] | CS = CN + CV
| CO2 in chloroplast | 848.7 | ppm | 1527.5799 | mg/m3
| Tm | 25 | [5 empty] | Photosynthesis | 0.16002 | mg/(m2.s)
| a | 5 |  | Kpr | 0.11737 |  |  | Photorespiration | 0.018781 | mg/(m2.s)
| Rd(20C) | 0.07 |  | Rd | 0.098995 | mg/(m2s) |  | Net Photos. | 0.042245 | mg/(m2.s) | Water balance
Environment |  | Temp. oC | RH, % | Rhoair,kg/m3 | h, kJ/kg | Vps | [5 empty] | Transpiration rate of room (TR) |  | 6.2777 | mg/(s.room)
| Indoor | 25 | 80 | 1.1442 | 65.8127 | 3.1674 |  | Vd in | 18.4076 | g/m3 |  | Water loss by ventilation (VW) |  | 43.5854 | mg/(s.room)
| Outdoor | 5 | 40 | 1.2674 | 10.4261 | 0.87226 |  | Vd out | 2.7169 | g/m3 |  | Dehumidification (D) |  | 0 | mg/(s.room)
| CO2 in (ppm) | 1000 | = | 1799.9056 | mg/m3 |  |  | Rlv | 1060 | s/m |  | Humidification (H) |  | 37.3077 | mg/(s.room)
| CO2 out (ppm) | 380 | = | 733.1702 | mg/m3 |  |  | Rav | 100 | s/m |  | TR+H = D + VW | H = D + VW - TR
| Wind (m/s) | 1 | m/s |  |  |  |  | Inc. of Rlv | 306.1064 | s/m
| Conductivity of walls | 0.1 | [5 empty] | TR | 3.1389 | mg/(m2.s)
Culture room
| Room length | 10 | m | Room volume |  | 500 | m3 | Leaf area per plt | 0.02 | m2/plt | Energy balance
| Room width | 10 | m | All 6 wall area |  | 400 | m2 | No. of plants | 100 | plt/room |  | Total W of lamps (WL) |  | 8000 | W/room
| Room height | 5 | m | ACH |  | 0.02 | 1/h |  |  |  |  | Total W of other equipment (We) |  | 80 | W/room
Lighting | [11 empty] | Heat loss by ventilation (Qv) |  | 176.0388 | W/room
| W per lamp | 20 | W/lamp | No. of lamps | 400 | #/room |  | Total W of lamps | 8000 | W/room |  | Heat loss by conduction (Qc) |  | 800 | W/room
| W of other equip. | 80 | W/room | PAR | 11.2 | W/m2 | [5 empty] | Heat carry away by AC (Qa) |  | 7103.9612 | W/room
WL + We = Qv + Qc + Qa